## العرض الفني
Specefcation |  | VENDER ITEM DESCRIPTION | COMMENTS | WHERE TO FIND
|  |  |  | OFFER PAGE NO | CATALOUGE PAGE NO
True on line, double conversion technology (80KVA)/
INPUT PFC ≥ 0.99
Wide input voltage range
Total harmonic distortion <5%
Compatible with E.G. operation
Contain built in static and manual by pass
Standard communication interface with (BMS) and generator port
INPUT specs. | phase (3 phase +N+PE)
Nominal voltage (380V-415V)
Nominal Frequency (50) HZ
Frequency range (45-55)Hz
Output specs. | phase (3 phase +N+PE)
Output P.F (1.00)
Nominal voltage (380V) (400V) (415V) (can be adjustable via display)
Static voltage regulation at (100%) load <1%
Frequency range ±2%
Over load (125% for not less than 10 min on invertor mode) (150% on bypass mode for not less than 1 minute on bypass mode)
Efficiency not less than (95%)
Battery specs. | Type free maintenance lead acid battery
Back up time not less than (15) minutes at full load/ 80 KVA/80KW
Submit the calculations To mit the backup time
Operatig Temperature (15-25)°C
على الشركة تعبئة هذا الكشف وبيان مدى موافقة الاجهزة المعروضة من قبلة للمواصفات المطلوبة وبيان المعلومات التي تثبت ذلك بحيث يتم وضع علامة (X) أمام المواصفة اذا كانت مطابقة للمطلوب و(XX) اذا كانت غير مطابقة وحسب الأعمدة أعلاه.
على الشركة التقدم بعرض مالي منفصل للأجهزة المطلوبة.